## Leakage Current
Leakage Current and Capacitance Discharge Calculator for X caps and Y caps
The selection of an AC line filter influences how a piece of equipment will perform during product safety tests. Specifically, capacitance discharge is an issue of the X capacitance of the filter. Leakage current is primarily a function of the Y capacitance. Enter the value of the X capacitors and Y capacitors implemented in the line filter you are considering to get an idea of how the filter will perfom during a safety analysis.
Total nominal X capacitance: | 4 | uF
Total nominal shunt resistance: | 400 | kOhms | Use 10 M Ohms if there is no shunt resistance (probe resistance).
Nominal, one branch, Y capacitance: | 1000 | nF
Mains voltage (worst case): | 240 | V rms
Mains frequency (worst case): | 60 | Hz
With these values the results of your safety tests will look approximately like those shown below.
Leakage current from line to ground: | 90.4779 | mA | Common limits are .75mA for ungrounded equipment, and 3.5mA for grounded equipment.
Time constant of capacitance discharge: | 1.6 | s | Normally, the voltage across the plug pins must be less than
Peak voltage across pins after one second: | 181.6738 | V peak | 125.5822 | V peak | one second after being disconnected
Voltage across pins after ten seconds: | 0.65522 | V peak | from the supply. Industrial twist lock connectors must comply with the same limit, but ten seconds after disconnection from their supply.